| Sr. | Item |  | Unit | Qty. |  |  |  | Rate (Rs.) |  | Amount (Rs.) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Shifting/re-lamination of old furniture- |  |  |  |  |  |  |  |  |  |
| 1.1 | Re-lamination, shifting, repairing of existing tables from old premises to new premises with inside painting. This item includes cutting, fitting of tables as per layout. |  | Nos. | 10 |  |  |  |  |  |  |
| 1.2 | Re-lamination, shifting, repairing of existing backside storage from old premises to new premises with inside painting. This item includes cutting, fitting of storage as per layout. |  | Sqft | 25 |  |  |  |  |  |  |
| 1.3 | Re-lamination, shifting, repairing of existing side storage from old premises to new premises with inside painting. This item includes cutting, fitting of storage as per layout. |  | Sqft | 20 |  |  |  |  |  |  |
| 1.4 | Customer writing Ledge/Cheque Drop Box - Shifting, repairing, re-lamination of customer writing ledge and cheque drop box, from old premised to new premises. |  | Nos. | 1 |  |  |  |  |  |  |
| 1.5 | Lamination of existing doors: - Re lamination of existing doors with matching laminate of branch. |  | SQFT | 20 |  |  |  |  |  |  |
| 1.6 | Extra for 20’’sliding channel pair for work station drawer.(Set = Pair of 2 channels) |  | SET | 1 |  |  |  |  |  |  |
| 1.7 | Extra for 16’’sliding channel pair for side storage.(Set = Pair of 2 channels) |  | SET | 1 |  |  |  |  |  |  |
|  |  |  |  | Total of 1(Rs.) |  |  |  |  |  |  |
| 2 | Procurement new of furniture and renovation items |  |  |  |  |  |  |  |  |  |
| 2.1 | P/F Solid Wooden/ Partly Glazed Partitions (BM cubicle, Cash cabin, partition wall) Basic frame work: 2’’ x 1.5’’ Salwood/ aluminium sections at maximum 600 mm horizontal & vertical Spacing as per site conditions. Wooden/ aluminum members of partitions shall be rigidly fixed to the Ceiling, Floors, Beams, Doors & the Side Walls, whichever is applicable. The frame work shall be coated with anti-termite treatments or chemicals. Skin Membrane: Single layered 6 mm thick MR grade plywood on each face. Finishing: Both side finished with 1 mm thick laminate sheet of same or combination shades as per instruction with 4’’ high skirting at top & bottom of Bank’s pattern (Blue & Red). Glass- 8mm for solid, 12mm for low height partition Cash cabin front partition – toughened 12mm glass partition as per direction. The open edges are to be blocked by teak wood bead of required size and design. All provisions to be made for all electrical, networking boxes onto partition framework at required heights/levels with necessary additional supports as directed. |  | SQFT | 300 |  |  |  |  |  |  |
| 2.2 | P/F Solid Cement sheet Partitions including doors (Server room, UPS room) Basic frame work: 2’’ x 1.5’’ aluminum sections at maximum 600 mm horizontal & vertical Spacing as per site conditions. Aluminum members of partitions shall be rigidly fixed to the Ceiling, Floors, Beams, Doors & the Side Walls, whichever is applicable. Skin Membrane: Single layered 12 mm thick cement sheet on each face. Finishing: Both side finished with putty, primer and 2 coats of OBD paint. Door- 675x 2100mm door with above specifications and all necessary hardwares. |  | SQFT | 140 |  |  |  |  |  |  |
| 2.3 | Grid False Ceiling- Providing and fixing of false ceilings at all heights of 600 mm X 600 mm X 16 mm Armstrong 15mm exposed/Silhouette grid system. The framework compromise of main runner spaced at 1200mm centers securely fixed to the structural soffit by approved hangers at 1200mm maximum centers. Hangers (GI wire of 4.0mm dia) to be fixed by approved roof plug, level adjuster and screws etc. The last hanger at the end of each main runner should not be greater than 450mm from the adjacent wall. Flush fitting 1200mm long cross tees (with double stitching) to be interlocked between main runners at 600mm centers to form 1200 X 600mm modules. Cut cross tees longer than 600mm to be supported independently. 600mm X 600mm modules to be formed by fitting 600mm long flush fitting cross tees centrally between the 1200mm cross tees. |  | SQFT | 600 |  |  |  |  |  |  |
| 2.4 | Gypsum Board False Ceiling: Providing and fixing Gypsum Board False Ceiling with 12mm thick Gypsum board and GI framing comprising of ceiling channel 80mm x 26mm x 0.5mm @ every 457 mm centre, intermediate channel 45mm x 15xmm x 0.8mm @ every 1200 mm centre, perimeter channel 20mm x 28mm x30mm x 0.5mm all along wall/partition, ceiling angle 25mm x 10mm x0.5 mm and other required fasteners/hardware like, soffit cleats, dash fasteners, nuts, clips, screws etc. The work includes taping and jointing, applying primer, two or more coats of emulsion paint of approved shade / make, making cut-out for light fixtures, etc. The Final coat shall be done with foam roller, and no brush marks should be visible. |  | SQFT | 700 |  |  |  |  |  |  |
| 2.5 | Toughened Glass partition with one Main Door: - Providing and fixing of 12 mm thick toughened glass partition and one main door of approved make with all SS patch fittings complete. Door item to include lock, pair of 300 mm long D handles and other necessary hardware of Stainless Steel of make all complete and excluding floor spring and pivot. |  | SQFT | 50 |  |  |  |  |  |  |
| 2.6 | Toughened Glass Door: - Providing and fixing of 12 mm thick toughened glass door approved make with all SS patch fittings complete. Door item to pair of 300 mm long D handles and other necessary hardware of Stainless Steel of make all complete and excluding floor spring and pivot. |  | SQFT | 21 |  |  |  |  |  |  |
| 2.7 | Providing and fixing of floor spring and pivot set for main door.(One floor Spring + pivot set = 1 set) |  | SET | 1 |  |  |  |  |  |  |
| 2.8 | Wooden paneling: Fabricating and fixing wall/column paneling to consist of 37.5mm x 50mm treated salwood framework or Aluminum Sections at spacing not exceeding 600mm bothways (horizontal and vertical). Paneling framework to be secured to wall surface/column surface. Paneling framework to be clad on one side with 6 mm thick MR grade ply finished with 1.0mm thk laminate including border / skirting of 100mm high & 1.5 mm x 1.5 mm groove at border/ skirting level |  | SQFT | 190 |  |  |  |  |  |  |
| 2.9 | ALLUMINIUM CLADDING: Design, Supply, Fabrication and installation / Fixing of Aluminium Composite Panels of approved make for external cladding and canopy cladding in combination of solid / Metallic colours, including all necessary frame work and complete weather sealing. The composite panel should consist of 3 mm LDPE sandwiched between 2 skins of 0.5mm thick Aluminium sheet making a total panel thickness of 4 mm. The supporting framework shall be made to suit the grid requirement at site out of extruded section 38x38x3mm aluminium angle section or 50x25x1.6mm tube section running vertically or horizontally fixed to building structure through M.S clamps prefixed to masonry with suitable anchor fastener or screws as required after aligning the framework for level and lines. the ACP panel cut to size and bent at edges to form a tray to be fixed to aluminium grid tubes cleats, angles etc with metal screws. All hardware will be corrosion resistant. The gaps will be sealed using weather sealant like Dow Corning 789 or any other approved brand. Note: the external surface shall be well protected with self adhesive peel off ma |  | SQFT | 110 |  |  |  |  |  |  |
| 2.10 | Branding Strip (4.5’’-5’’ wide below false ceiling):- Providing and fixing wall strip over the existing wall madeup of 12 mm thick ply of approve make finish with 1.0 mm thick mica of approve make & shade. Open edges shall neatly finished. |  | RFT | 120 |  |  |  |  |  |  |
| 2.11 | Doors/Wicket doors:- Providing and fixing of 35mm solid core flush door with both side laminated with approved laminate and all necessary hardware and handle, lock. For wicket door 18mm thick MR Ply and both side laminate door with necessary hardwares. |  | SQFT | 40 |  |  |  |  |  |  |
| 2.12 | Electrical Panel Cabinet with door: Providing and fixing Electric Panel Cover box as per drawing made of 18 mm thick Ply finished with 1.0 mm thick laminate in front side and paint inside all Complete with hardware fittings. There shall be provision for air ventilation. |  | SQFT. | 25 |  |  |  |  |  |  |
| 2.13 | Notice Board: Providing and fixing notice board of 4'-0''X2'-6'' size in ply board of 6mm fixed on a frame of 50 mm x 25 mm well-seasoned wood polished and top fixed with bead. 12mm thk. Soft board cladded with fabric of matching colour and shade complete with all fixtures necessary as required |  | Nos. | 1 |  |  |  |  |  |  |
| 2.14 | Providing and fixing of door closer. |  | Nos. | 2 |  |  |  |  |  |  |
| 2.15 | Providing and fixing of 16-18’’ wide side storage cabinet with 19mm MR grade ply and 6mm backply. All external surfaces is laminated with 1mm approved laminate and 6mm lipping patti with polish. Internal surface to be painted. Side storage shall contain 2 drawer unit and1 storage units containing one shelve and 2 door shutters. This item also includes all necessary hardware, handle and locks. (Payment made for Length x Height) |  | Sqft. | 7.5 |  |  |  |  |  |  |
| 2.16 | Backside storage- Providing and fixing of Back side storage with specifications same as above but without drawer. |  | Sqft. | 7.5 |  |  |  |  |  |  |
|  |  |  |  | Grand Total of 2 (Rs.) |  |  |  |  |  |  |
|  | Item |  | Unit | Qty. |  |  | Rate(Rs.) |  |  | Amount(Rs.) |
| 3 | Supply, Installation, Testing, Commission of Electrical Fixtures. |  |  |  |  |  |  |  |  |  |
|  | Supplying, installation with hanging support, testing and commissioning of following light fixtures with electronic Ballasts, Tubes, lamps, all fixing materials including connecting wires etc. all complete as per the directions of Engineer-in-charge. |  |  |  |  |  |  |  |  |  |
| 3.1 | 36 watt, 2800 lumens square 2’X 2' LED light with necessary fixtures. |  | Nos. | 13 |  |  |  |  |  |  |
| 3.2 | Shifting and Fixing of LED lights of existing Branch |  | Nos. | 5 |  |  |  |  |  |  |
| 3.3 | 14-15 w ,Minimum 850 lumens LED ROUND DOWN LIGHTER Diameter 110-165mm. |  | Nos. | 14 |  |  |  |  |  |  |
| 3.4 | 4feet long 20w Light batten plain fitting with acrylic cover complete |  | Nos. | 10 |  |  |  |  |  |  |
| 3.5 | 400 mm sweep Wall bracket fan of approved make complete. |  | Nos. | 5 |  |  |  |  |  |  |
| 3.6 | 1200 mm sweep Celling fan of approved make complete. |  | Nos. | 3 |  |  |  |  |  |  |
| 3.7 | 300 dia Exhaust Fan continuously rated, capacitor start and run type, totally enclosed and ruggedly built, pre lubricated double ball bearing, copper wounded, A & E class insulation, dynamically balanced, below 40 db sound level etc. |  | Nos. | 2 |  |  |  |  |  |  |
| 3.8 | 15w LED bulb |  | Nos. | 2 |  |  |  |  |  |  |
| 3.9 | ding dong bell |  | Nos. | 1 |  |  |  |  |  |  |
| 3.10 | Fan hook & Fan Rod, |  | Nos. | 2 |  |  |  |  |  |  |
|  |  |  |  |  |  |  | Total of 3= |  |  |  |
| 4 | Electric wiring and Switches |  |  |  |  |  |  |  |  |  |
|  | Item | Unit |  |  | Qty. | Rate(Rs.) |  |  | Amount(Rs.) |  |
| 4.1 | Main Panels and Distribution Boards |  |  |  |  |  |  |  |  |  |
| a | Main Panel Box (415V, 3-Ph, 4 wire) :- Supply, installation , testing and commissioning of totally enclosed compartmentalized dust and vermin proof cubical segregated and modular in construction M.V. panel board wall mounted fabricated with 16swg of CRCA M.S. sheet duly painted with two coat of metal red oxide and two coat of fire resistance paint at inside and outside of the panel, cable entry from top and bottom, glande plate of 3mm thickness, bus-bar chamber ,outgoing switchgear etc (all feeder unit Would be compartmentalized), vertical / horizontal busbar of required size of length, ( bus-bar distances shall be minimum 32 mm ) insulators, hardware, neoprene gasket , hinged door, interconnecting single core multi strand lugged copper wire having current density of 2A / sqmm of suitable capacity & size with lugs from busbar to switchgears / MCCB / MCB or where ever required. Incomer:- 1 Nos. 125 Amp MCCB, 25 KA- 4 Pole, C-curve, 1 Nos. 63 A TPN MCB,C-curve 1 Nos. 200 A TPN insulated Copper Bus Bar, Set of R-Y-B Phase indicating lamp, 1 Set. Digital Voltmeter, Ammeter, frequency meter Outgoing:- 4 Nos -63 A TPN MCB,C-curve 1 Nos.- 40 A TPN MCB(ATM) 1 Nos.- 25 A MCB (Glow sign board) Set as above | Nos. |  |  | 1 |  |  |  |  |  |
| b | Supply and fixing of TPN 125 A Switch Fuse Unit (SFU) with HRC fuse in sheet steel enclosure on M.S. angle frame / M.S. legs on wall complete with interconnection, mending good damages to original finish, painting, etc" as required. | Nos. |  |  | 1 |  |  |  |  |  |
| c | Distribution Boards:- Supply, Installation, Testing and commissioning of the surface / recess mounting following way TPN MCB three phase distribution board for Light/Power/AC and UPS separately including neutral, earth bars, direct on wall incl. electrical connection ,earthing , making good all the damages, painting, cleaning the site, etc complete as per site requirement and as directed including the followings accessories- |  |  |  |  |  |  |  |  |  |
| c1 | Light Distribution & Power Distribution Board( 8 way TPN single door) Incomer:- 1 No. 63 Amp 100 ma sensitivity RCCB 4 Pole 3 No. 32 Amp DP MCB Outgoing:- 12 nos. 6 /10/16/20 Amp SP MCB Set as above | Nos. |  |  | 1 |  |  |  |  |  |
| c2 | AC Distribution Board:- ( 4 way distribution TPN single door) Incomer:- 1 No. 63 Amp TPN MCB Outgoing:- 6 nos. 25Amp DP MCB Set as above | Nos. |  |  | 1 |  |  |  |  |  |
| c3 | UPS (Input/Output) Incomer:- 1 No. 40 Amp TPN MCB 2 No. 63 Amp DP MCB Set as above | Nos. |  |  | 1 |  |  |  |  |  |
| c4 | UPS Power Distribution Board : ( 8 way distribution SPN single door) 1 No. 40 Amp DP MCB 4 nos. 16/20 Amp SP MCB Set as above | Nos. |  |  | 1 |  |  |  |  |  |
| 4.2 | Earthing System |  |  |  |  |  |  |  |  |  |
| a | Providing chemical or dedicated earthing with 600x600x3.15mm copper plate along with 50mm dia.10feet long G.I pipe with other accessories in the earth filled with necessary salt, charcoal, etc. It should be covered with G.I Manhole cover with necessary civil works etc. complete. | Nos. |  |  | 2 |  |  |  |  |  |
| b | Supply & Laying of 8SWG copper wire from earth station to UPS and lighting MCB DB. | Mtr. |  |  | 25 |  |  |  |  |  |
| c | 25 mm heavy duty PVC conduit. | Mtr. |  |  | 10 |  |  |  |  |  |
| 4.3 | Cables and cable laying |  |  |  |  |  |  |  |  |  |
|  | LT Cables:-Supply & Laying of the following cables in built up trenches, on wall, or in the ground as per the case may be, with proper clamping with necessary fixing materials etc. Installing, testing & commissioning of 1100V grade UG cable with GI wires as per IS 7098/1554 |  |  |  |  |  |  |  |  |  |
| a | 3.5C X 35 Sq.mm AYFY ALU armored cable ( Main) | Mtr. |  |  | 20 |  |  |  |  |  |
| b | 4c X 10 Sq.mm copper armored cable (Main panel to UPS, & AC DB) | Mtr. |  |  | 25 |  |  |  |  |  |
| c | 4c X 16 Sq.mm copper armored cable (ATM) | Mtr. |  |  | 10 |  |  |  |  |  |
| d | 2 x 6 Sq.mm + 1x 2.5 Sq.mm FR PVC coated copper conductors (1.1 KV grade) in pvc rigid pipe/capping-casing on surface of wall duly clamping with necessary fittings and accessories from Main DB to POWER/LIGHT DB. Including all necessary terminals etc complete. | Mtr. |  |  | 2 |  |  |  |  |  |
| 4.3.1 | Cable end termination:- |  |  |  |  |  |  |  |  |  |
| a | 3.5C X 25 Sq.mm AYFY ALU cable ( Main) | Nos. |  |  | 2 |  |  |  |  |  |
| b | 4c X 10 Sq.mm copper cable | Nos. |  |  | 2 |  |  |  |  |  |
| c | 4c X 16 Sq.mm copper cable (ATM) | Nos. |  |  | 2 |  |  |  |  |  |
| 4.4 | Internal wiring |  |  |  |  |  |  |  |  |  |
|  | Supply of all required materials and wiring to circuits/ submains with following number and sizes of FRLS PVC insulated 1100 volt grade standard copper wire run in suitable PVC conduit pipe of ISI mark with conduit accessories like bend , junction box etc in concealed/surface manner as per site as required and copper wire as earth continuity conductor and complete in all respect including making good to all damages caused, cleaning the site etc complete as required as per site requirement and as directed. |  |  |  |  |  |  |  |  |  |
| a | Providing and fixing of PVC tranking of 50mmx50mm | Mtr |  |  | 3 |  |  |  |  |  |
| b | Providing and fixing of PVC tranking of 50mmx50mm | Mtr |  |  | 3 |  |  |  |  |  |
| b | 2x 2.5 Sq mm + 1x1.5 Sq mm copper wire circuit mains for raw power points, lights and glow sign board. (LDB to Switch boards). For 16A power point maximum 2 points in a circuit. For 6 A power point maximum 3 point in a circuit. | Mtr |  |  | 150 |  |  |  |  |  |
| c | 2x 2.5Sqmm + 1x1.5 Sq mm copper wire for circuit mains (UPS DB to Computer) Maximum 3 workstations in circuit. | Mtr. |  |  | 50 |  |  |  |  |  |
| d | 2 x 4sqmm + 1x1.5 sq mm copper wire ( From AC DB to AC point) | Mtr. |  |  | 100 |  |  |  |  |  |
| 4.5 | Point Wiring |  |  |  |  |  |  |  |  |  |
|  | Point wiring with 1100 V grade 3 nos. single core 1.5 sq.mm PVC insulated flexible FRLS copper conductor cable (IS:694) through suitable size PVC conduit complete with junction box, circular box, elbows, bends, couplers and other accessories on surface above false ceiling or concealed by chase cutting on wall from light & fan switch board to light, fan & 6A socket outlet on the same switch board or separately mounted switch board. The work includes supply and fixing of all materials such as modular type 6A switch for each light and fan point, 6A 2/3 pin socket outlet with switch, 3 plate ceiling rose / angle or batten |  |  |  |  |  |  |  |  |  |
| a | 1 light point controlled by one switch | Nos. |  |  | 30 |  |  |  |  |  |
| b | 2 light point controlled by one switch | Nos. |  |  | 12 |  |  |  |  |  |
| c | Wall fan/Exhaust fan controlled by 6 Amp socket and switch on light switch board | Nos. |  |  | 9 |  |  |  |  |  |
| d | Call bell point | Nos. |  |  | 1 |  |  |  |  |  |
| e | Ceiling fan point with modular type regulator and switch. | Nos. |  |  | 2 |  |  |  |  |  |
| 4.6 | Power Point Outlets |  |  |  |  |  |  |  |  |  |
| a | 6A Raw Power Poin (On Board)t-Supply, Installation, Testing and commissioning of onboard modular switch board containing 1 no 5pin 6A socket with switch including cover plate, sheet steel box / PVC modular box etc. of approved make on table/wall. | Nos. |  |  | 10 |  |  |  |  |  |
| b | 6A Raw Power Point (Special)-Supply, Installation, Testing and commissioning of modular switch board containing 1 no 5pin 6A socket with switch including cover plate, sheet steel box / PVC modular box etc. of approved make on table/wall. | Nos. |  |  | 11 |  |  |  |  |  |
| c | 16A Raw Power Point-Supply, fixing, testing and commissioning of modular switch board containing 1 no. 16 A switch & 1 no. six pin 6/16 Amp. Multi Socket with cover plate, sheet steel /PVC modular box etc on surface / concealed manner. | Nos. |  |  | 2 |  |  |  |  |  |
| d | 6A UPS Power Point-Supply, fixing, testing and commissioning of 1 no. 6 A switch & 3 no. six pin 6 Amp. Socket with cover plate, PVC modular box etc on surface / concealed manner. | Nos. |  |  | 12 |  |  |  |  |  |
| e | AC Point- Supply & Installation of modular type AC box (tiny trip type) with 20 Amp. socket & 20A SP MCB complete to be provided near indoor unit. | Nos. |  |  | 7 |  |  |  |  |  |
| f | Timer for Glow sign Board -Supply, installation and testing of timer with contactor (L&T /Legrand) make controlling the glow sign board with all accessories complete as required as per direction of Engineer incharge. The system will be a part of the panel board. | Nos. |  |  | 1 |  |  |  |  |  |
| 4.7 | Telephone wiring |  |  |  |  |  |  |  |  |  |
| a | Supply & laying of 0.5mm dia. Tinned Copper 2 pair telephone cable in the prelaid data cable conduit. | Mtr. |  |  | 50 |  |  |  |  |  |
| b | Supply & Fixing of RJ 11 Telephone Sockets with PVC modular box and faceplate complete. | Nos. |  |  | 3 |  |  |  |  |  |
| c | Supply & Installation of 50Pair KRONE Box with Enclosure | Nos. |  |  | 1 |  |  |  |  |  |
|  |  |  |  |  | Total of 4 = |  |  |  |  |  |
| 5 | Data Cabling Works |  |  |  |  |  |  |  |  |  |
| 5.1 | Supply and lying of CAT6 Network cable in the PVC conduit | Mtr. |  |  | 200 |  |  |  |  |  |
| 5.2 | Supply and fixing of RJ45 Network socket with front plate and base box for computer workstations. | Nos. |  |  | 14 |  |  |  |  |  |
| 5.3 | Supply and fixing of 3 feet patch card | Nos. |  |  | 9 |  |  |  |  |  |
| 5.4 | Supply and fixing of 7 feet patch card | Nos. |  |  | 9 |  |  |  |  |  |
| 5.5 | Shifting, Testing, commissioning of router, patch panel, rack, modem, switch etc. from exiting branch to new premises. | LS |  |  | 1 |  |  |  |  |  |
|  |  |  |  |  | Total of 5 = |  |  |  |  |  |
|  | Item | Unit |  |  | Qty. | Rate(Rs.) |  |  | Amount(Rs.) |  |
| 6 | Shifting and copper piping of AC |  |  |  |  |  |  |  |  |  |
| 6.1 | Shifting of AC from old premises to new premises including uninstallation, reinstallation. |  |  |  |  |  |  |  |  |  |
|  | Split unit | No. |  |  | 7 |  |  |  |  |  |
| 6.2 | Supplying & Laying extra suitable Copper refrigerant piping with all required material including power cable from indoor to outdoor suitable for 1Tr/1.5 tr /2 tr load/AC. | rft |  |  | 250 |  |  |  |  |  |
| 6.3 | Supplying & Laying extra suitable PVC Drain piping with all required material. | rft |  |  | 60 |  |  |  |  |  |
| 6.4 | Supplying & Fixing suitable MS Stand for 1.5 tr/2 tr AC outdoor. | No. |  |  | 7 |  |  |  |  |  |
|  |  |  |  |  | Total of 6 = |  |  |  |  |  |

Summary of Total works-

| Sr.no. | Particular | Amount(Rs.) Excluding GST |
| --- | --- | --- |
|  | Furniture and renovation works- |  |
| 1 | Repair/shifting/renovation of existing furniture |  |
| 2 | Procurement of new renovation items(New work) |  |
|  | Electrical works- |  |
| 3 | LED, tube light, fans (New) |  |
| 4 | Electric wiring and switches |  |
| 5 | Data Cabling works (New) |  |
| 6 | Shifting of existing Air-condition machine and copper piping works |  |
|  | Total= |  |

Above rates and amounts are excluding GST and GST as applicable shall be charged extra.

Seal and signature of Contractor